## CONDUCTION
HEAT TRANSFER SPREADSHEET CALCULATIONS |  |  |  | 4 PDH
Copy write, © Heat Transfer Spreadsheet Calculations by John R Andrew, 12 June 2011
Rev: 3 Aug 2014
CONDUCTION
Heat travels three ways:
* Conduction - by spreading through solids.
* Convection is heat transfer by the movement of heated gasses and liquids.
* Radiation - is heat in the form of radiation and travels through space at the speed of light.
Heat always travels from an area of higher temperature to an area of lower temperature.
Heat transfer (Q) is the flow rate of heat and is measured in Watts or Btu's per hour.
When using Excel's Goal Seek, unprotect the spread sheet by selecting:
Drop down menu: Tools > Protection > Unprotect Sheet > OK
When Excel's Goal Seek is not needed, restore protection with:
Drop down menu: Tools > Protection > Protect Sheet > OK
UNITS
Symbol | Units | Multiply | Units
|  | by | Obtained
Q | Btu/hr | 0.2931 | W
Q | Btu/hr | 0.0003929 | hp
w | Btu | 778.2 | ft-lbf
K | Btu/hr-ft-deg F | 1.73 | W / m-C
h | Btu/hr-ft^2-F | 5.5956 | W / m^2-C
ρ | lbm/ft^2 | 16.0185 | kg / m^3
Cp | Btu/lbm-deg F | 4187 | J/kg-C
μ | lbm / sec-ft | 3600 | lbm / hr-ft
μ | lbm / sec-ft | 1.488 | kg / sec-m
L | ft | 0.3048 | m
L | in | 25.4 | mm
L | in | 0.0254 | m
F | lbf | 4.4482 | N
w | ft-lbf | 1.3558 | N-m
ν | ft^2 / sec | 0.0929 | m^2 / s
Heat transfer is measured in feet and meter units.
Use the above units table from left to right:
Input Data
Units = | 42
Multiply by = | 0.0254
Calculations
Units Obtained = | 1.0668
Use the above units table from right to left:
Input Data
Units Obtained = | 22
Divide by = | 5.5956
Calculations
Units = | 3.9317
Temperature is the intensity of heat: | Input Data |  |  | Input Data
T = | 52 | deg C | T = | 50 | deg F
T = | deg C + 273.2 |  | T = | deg F + 460
T = | 325.2 | deg K | T = | 510 | deg R
| Input Data |  |  | Input Data
T = | 62 | deg F | T = | 60 | deg C
T = | 5*(deg F - 32)/9 |  | T = | (9*deg C/5) + 32
T = | 16.6667 | deg C | T = | 140 | deg F
Conduction Example
Input Data
Heat source on t1 side, Q = | 12 | Watts
High temperature, t1 = | 100 | deg C
Thermal conductivity, K = | 111 | W / m-K
Dimension in inches, L1 = | 4 | in
Dimension in inches, L2 = | 4 | in
Thickness in inches, X = | 0.375 | in
Calculation
Area, A = | (L1*L2)*0.0254^2
Answer: A = | 0.010323 | m^2
Heat transfer, Q = | K*A*(t1 - t2) / (X*0.0254)
Low temperature, t2 = | t1 - (Q*X) / (K*A)
Answer: t2 = | 99.9002 | deg C
CONDUCTIVITIES & DENSITIES
Properties at 68 deg F
MATERIAL | ρ | K | K
| lbm/ft^3 | Btu/hr-ft-F | W/m*C
Copper, pure | 559 | 223 | 386
Brass, 70 Cu, 30 Zn | 532 | 64 | 111
Silver, 99.9% pure | 657 | 235 | 407
Duralumin, 3-5%Cu, trace Mg | 174 | 95 | 164
Carbon Steel, 1.0%C | 487 | 25 | 43
Bronze, 75 Cu, 25 Sn | 541 | 15 | 26
Stainless Steel,18 Cr, 8 Ni | 488 | 9.4 | 16.3
Concrete, stone, 1-2-4 mix |  | 0.79 | 1.37
Glass, window |  | 0.45 | 0.78
Brick, common building |  | 0.4 | 0.69
Wood, fir |  | 0.063 | 0.109
Wood, white pine |  | 0.065 | 0.112
Glass Wool, 1.5 lb/ft^3 |  | 0.022 | 0.038
Heat Transmission Through Air Films and Solids
Conduction through wall and air films on each side of the wall.
Find the heat transfer rate Q and the inner and outer wall surface temperatures.
OVERALL HEAT TRANSFER COEFFICIENT U
The heat flow rate, Q, is the same through each layer in the diagram above.
Thermal Resistances of Layers
Heat transfer per unit area, Q / A = | (t1 - t2) / (Xa / Ka) |  | Equation 1
Heat intensity = | t1 -t2
Thermal resistance for layer a, Ra = | Xa / Ka
Thermal resistance for layer o, Ro = | 1/ ho
Overall heat transfer rate, Q / A = | (t1 -t4) / (Ra + Rb + Rc)
Overall temperature difference, ∆T= | t1 - t4
Overall heat transfer coefficient, U = | 1 / (A * Σ Rn)
Heat transfer per unit area, Q / A = | U*(∆T)
U.S. Units | Input Data |  |  |  |  | Metric Units | Input Data
Wall length, L = | 300 | in |  |  |  | Wall length, L = | 300 | in
Wall height, H = | 48 | in |  |  |  | Wall height, H = | 48 | in
Wall thickness, X = | 7 | in |  |  |  | Wall thickness, X = | 6 | in
Inside convective coefficient, ho = | 2 | Btu/hr-ft^2-F |  |  |  | Inside convective coefficient, ho = | 9.38 | Btu/hr-ft^2-F
to = | 70 | deg F |  |  |  | to = | 22.2 | deg F
t5 = | 36 | deg F |  |  |  | t5 = | -1 | deg F
Thickness, Xa = | 1 | in |  |  |  | Xa = | 1 | in
Xb = | 4 | in |  |  |  | Xb = | 0.66 | in
Xc = | 0.75 | in |  |  |  | Xc = | 0.5 | in
Thermal conductivity, Ka = | 0.065 | Btu/hr-ft-F |  |  |  | Ka = | 0.1 | Btu/hr-ft-F
Thermal conductivity, Kb = | 0.4 | Btu/hr-ft-F |  |  |  | Kb = | 0.1 | Btu/hr-ft-F
Thermal conductivity, Kc = | 0.28 | Btu/hr-ft-F |  |  |  | Kc = | 0.52 | Btu/hr-ft-F
Outside convective coefficient, h5 = | 5.8 | Btu/hr-ft^2-F |  |  |  | Outside convective coefficient, h5 = | 34.1 | Btu/hr-ft^2-F
| Calculation | [5 empty] | Calculation
Wall area, A = | L*H / 144 |  |  |  |  | Wall area, A = | L*H*0.0929 / 144
A = | 100 | ft^2 |  |  |  | A = | 9.29 | m^2
Thermal Resistances | [5 empty] | Thermal Resistances:
Ro = | 1 / ho |  |  |  |  | Ro = | 1 / ho
Ro = | 0.5 |  |  |  |  | Ro = | 0.10661
Ra = | Xa / Ka |  |  |  |  | Ra = | Xa / Ka
Ra = | 1.2821 |  |  |  |  | Ra = | 0.254
Rb = | Xb / Kb |  |  |  |  | Rb = | Xb / Kb
Rb = | 0.83333 |  |  |  |  | Rb = | 0.16764
Rc = | Xc / Kc |  |  |  |  | Rc = | Xc / Kc
Rc = | 0.22321 |  |  |  |  | Rc = | 0.024423
R5 = | 1 / h5 |  |  |  |  | R5 = | 1 / h5
R5 = | 0.17241 |  |  |  |  | R5 = | 0.029326
Overall heat transfer coefficient | [5 empty] | Overall heat transfer coefficient
1 / U = | 1/ho + Xa / Ka + Xb / Kb + Xc / Kc + 1/h5 |  |  |  |  | 1 / U = | 1/ho + Xa / Ka + Xb / Kb + Xc / Kc + 1/h5
1 / U = | Ro+R1+Ra+Rb+Rc+R5 |  |  |  |  | 1 / U = | Ro+R1+Ra+Rb+Rc+R5
1 / U = | 3.011 |  |  |  |  | 1 / U = | 0.582
Answer: U = | 0.33211 |  |  |  |  | Answer: U = | 1.7182
∆T = | to - t5 |  |  |  |  | ∆T = | to - t5
Answer: ∆T = | 34 | deg F |  |  |  | Answer: ∆T = | 23.2 | deg C
Heat transfer per unit area, Q / A = | U*(∆T) |  |  |  |  | Heat transfer per unit area, Q / A = | U*(∆T)
Answer: Q / A = | 11.2919 |  |  |  |  | Answer: Q / A = | 39.8627
Heat transfer, Q = | U*A*(∆T) |  |  |  |  | Heat transfer, Q = | U*A*(∆T)
Answer: Q = | 1129.1882 | Btu/hr |  |  |  | Answer: Q = | 370.324 | Watts
Answer: Q = | 330.9651 | Watts
Surface temperature is found from Equation-1 above: | [5 empty] | Surface temperature is found from Equation-1 above:
Heat transfer per unit area, Q / A = | (to - t1) / (1 / ho) |  |  |  |  | Heat transfer per unit area, Q / A = | (to - t1) / (1 / ho)
t1 = | to - (Q/A)*(1 / ho) |  |  |  |  | t1 = | to - (Q/A)*(1 / ho)
Answer: t1 = | 64.3541 | deg F |  |  |  | Answer: t1 = | 17.9503 | deg F
Internal temperature follows: | [5 empty] | Internal temperature follows:
Heat transfer per unit area, Q / A = | (t1 - t2) / (Xa / Ka) |  |  |  |  | Heat transfer per unit area, Q / A = | (t1 - t2) / (Xa / Ka)
t2 = | t1 - (Q/A)*(Xa / Ka) |  |  |  |  | t2 = | t1 - (Q/A)*(Xa / Ka)
Answer: t2 = | 49.8773 | deg F |  |  |  | Answer: t2 = | 7.8251 | deg F
Thermal Resistances of Layers - continued
Input Data
Wall length, L = | 12 | in
Wall height, H = | 12 | in
Wall thickness, X = | 0.5 | ft
Inside temperature, t1 = | 70 | deg F
Outside temperature, t4 = | 20 | deg F
Wall material conductivity, K = | 0.26315 | Btu/hr-ft-F
Inside convective coefficient, ha = | 2 | Btu/hr-ft^2-F
Outside convective coefficient, hc = | 10 | Btu/hr-ft^2-F
Calculations
Wall area, A = | L*H / 144
A = | 1 | ft^2
Ra = | 1 / ha
Ra = | 0.5
Rb = | X / K
Rb = | 1.9
Rc = | 1 / hc
Rc = | 0.1
Overall thermal resistance, R = | Ra + Rb + Rc
ΣR = | 2.5
Overall temperature difference, ∆T = | t1 - t4
∆T = | 50 | deg F
Heat transfer per unit area, Q / A = | ∆T / ΣR
Q / A = | 19.9998 | Btu / hr-ft^2
Heat transfer, Q = | A*∆T / ΣR
Q = | 19.9998 | Btu/hr
Q = | 5.8619 | Watts
Internal temperatures are found from Equation-1 above:
Heat transfer per unit area, Q / A = | (t1 - t2) / (Ra)
t2 = | t1 -(Q/A)*(Ra)
Answer: t2 = | 60.0001 | deg F
Heat transfer per unit area, Q / A = | (t3 - t4) / (Rc)
t3 = | t4 + (Q/A)*(Rc)
Answer: t3 = | 22 | deg F
2D HEAT TRANSFER
EXCEL'S SOLVER > see MATH TOOLS tab below.
The steady state energy balance on the interior nodal point N is:
0 = | Q1-N + Q2-N + Q3-N + Q4-N
L = | Thickness into page.
Finite difference equations for each conductive flux:
Q1-N = | K*L*(∆Y)*(T1 - TN) / (∆X)
Q2-N = | K*L*(∆X)*(T2 - TN) / (∆Y)
Q3-N = | K*L*(∆Y)*(T3 - TN) / (∆X)
Q4-N = | K*L*(∆X)*(T4 - TN) / (∆Y)
If ∆X equals ∆Y:
0 = | T1 +T2 + T3 + T4 -4*TN
Node 1, 0 = | 400 + 500 + T2 + T4 - 4*T1 |  |  |  |  | Node 1, 0 = | 300 + 400 + T2 + T4 - 4*T1
Node 2, 0 = | T1 + 500 + 200 + T3 - 4*T2 |  |  |  |  | Node 2, 0 = | T1 + 400 + 100 + T3 - 4*T2
Node 3, 0 = | T4 + T2 + 200 + 300 - 4*T3 |  |  |  |  | Node 3, 0 = | T4 + T2 + 100 + 200 - 4*T3
Node 4, 0 = | 400 + T1 + T3 + 300 - 4*T4 |  |  |  |  | Node 4, 0 = | 300 + T1 + T3 + 200 - 4*T4
Node 1, -900 = | T2 + T4 - 4*T1 |  |  |  |  | Node 1, -700 = | T2 + T4 - 4*T1
Node 2, -700 = | T1 + T3 - 4*T2 |  |  |  |  | Node 2, -500 = | T1 + T3 - 4*T2
Node 3, -500 = | T4 + T2 - 4*T3 |  |  |  |  | Node 3, -300 = | T4 + T2 - 4*T3
Node 4, -700 = | T1 + T3 - 4*T4 |  |  |  |  | Node 4, -500 = | T1 + T3 - 4*T4
| Equations | Constants | Solution | Column E |  |  | Equations | Constants | Solution | Column E
Node 1 | -900 | -900 | T1 = | 400 | deg C | Node 1 | 0 | -700 | T1 = |  | deg C
Node 2 | -700 | -700 | T2 = | 350 | deg C | Node 2 | 0 | -500 | T2 = |  | deg C
Node 3 | -500 | -500 | T3 = | 300 | deg C | Node 3 | 0 | -300 | T3 = |  | deg C
Node 4 | -700 | -700 | T4 = | 350 | deg C | Node 4 | 0 | -500 | T4 = |  | deg C
CLICK THE "MATH TOOLS" TAB BELOW FOR INFORMATION ABOUT "SOLVER"
| Equations | Constants | Solution | Column E
Node 1 | 0 | -900 | T1 = |  | deg C
Node 2 | 0 | -700 | T2 = |  | deg C
Node 3 | 0 | -500 | T3 = |  | deg C
Node 4 | 0 | -700 | T4 = |  | deg C
Node 1, 0 = | 400 + 100 + T2 + T4 - 4*T1
Node 2, 0 = | T1 + 100 + T3 + T5 - 4*T2
Node 3, 0 = | T2 + 100 + 100 + T6 - 4*T3
Node 4, 0 = | 400 + T1 + T5 + T7 - 4*T4
Node 5, 0 = | T4 + T2 + T6 + T8 - 4*T5
Node 6, 0 = | T5 + T3 + 100 + T9 - 4*T6
Node 7, 0 = | 400 + T4 + T8 + 200 - 4*T7
Node 8, 0 = | T7 + T5 + T9 + 200 - 4*T8
Node 9, 0 = | T8 + T6 + 100 + 200 - 4*T9
Node 1, -500 = | T2 + T4 - 4*T1
Node 2, -100 = | T1 + T3 + T5 - 4*T2
Node 3, -200 = | T2 + T6 - 4*T3
Node 4, -400 = | T1 + T5 + T7 - 4*T4
Node 5, 0 = | T4 + T2 + T6 + T8 - 4*T5
Node 6, -100 = | T5 + T3 + T9 - 4*T6
Node 7, -600 = | T4 + T8 - 4*T7
Node 8, -200 = | T7 + T5 + T9 - 4*T8
Node 9, -300 = | T8 + T6 - 4*T9
| Equations | Constants | Solution | Column E
Node 1 | -500 | -500 | T1 = | 235.7143 | deg C
Node 2 | -100 | -100 | T2 = | 166.0714 | deg C
Node 3 | -200 | -200 | T3 = | 128.5714 | deg C
Node 4 | -400 | -400 | T4 = | 276.7857 | deg C
Node 5 | 0 | 0 | T5 = | 200 | deg C
Node 6 | -100 | -100 | T6 = | 148.2143 | deg C
Node 7 | -600 | -600 | T7 = | 271.4286 | deg C
Node 8 | -200 | -200 | T8 = | 208.9286 | deg C
Node 9 | -300 | -300 | T9 = | 164.2857 | deg C
BOUNDARY CONDITIONS
0 = | (T1 + T2)/ 2 + (h*∆X / k)*T∞ - (h*∆X / k + 1)*Tn
Input Data
Ambient temperature, T∞ = | 90
Convective heat transfer coefficient, hc = | 9.1
Conductivity, k = | 2
Grid spacing, ∆X = ∆Y = | 1.5
0 = | T1 + T4 + (T2 + T3)/ 2 + (h*∆X / k)*T∞ - (h*∆X / k + 3)*Tn
0 = | (T1 + T2)/ 2 + T3 - 2*Tn
0 = | T1 / a*(a + 1) + T2 / (b + 1) + T3 / (a + 1) + T4 / b*(b + 1)
- (1/a + 1/b)*Tn
Linear Thermal Expansion
| Input Data | Units | or
Length, L = | 120 | in | mm
Material Coefficient, α = | 1.2e-05 | in/in | mm/mm
Temperature Change, Δt = | 100 | deg F | deg C
Coefficients of Linear Expansion | in the range 0 to 100C
Aluminum α = | 2.38e-05
Bronze α = | 1.75e-05
Copper α = | 1.65e-05
Mild Steel α = | 1.2e-05
Porcelain α = | 4e-06
Calculations
Length change, ΔL = | L * α * Δt
Answer: ΔL = | 0.144 | in or mm
This is the end of this spread sheet.
Spread Sheet Method: new Excel version
1. Type in values for the Input Data.
2. Excel will make the Calculations.
Excel's GOAL SEEK
Excel's, "Goal Seek" adjusts one Input value to cause a Calculated formula cell to equal a given value.
When using Excel's Goal Seek, unprotect the spread sheet by selecting: Drop down menu: Home > Format > Unprotect Sheet > OK
When Excel's Goal Seek is not needed, restore protection with:
Drop down menu: Home > Format > Protect Sheet > OK
Spread Sheet Method: Excel-97 2003 - old version
1. Type in values for the Input Data.
2. Excel will make the Calculations.
Excel's GOAL SEEK
Excel's, "Goal Seek" adjusts one Input value to cause a Calculated formula cell to equal a given value.
When using Excel's Goal Seek, unprotect the spread sheet by selecting: Drop down menu: Tools > Protection > Unprotect Sheet > OK
When Excel's Goal Seek is not needed, restore protection with:
Drop down menu: Tools > Protection > Protect Sheet > OK

## CONVECTION
HEAT TRANSFER SPREADSHEET CALCULATIONS |  |  | 4 PDH
Copy write, © Heat Transfer Spreadsheet Calculations by John R Andrew, 12 June 2011
CONVECTION
Convection is heat transfer by the movement of heated gasses and liquids.
Measuring Air Film Coefficient | Input Data
Heat source, Q = | 100 | Watts
Surface area, A = | 0.4 | sq m
Inside air temp. thermocouple, t1 = | 65.3 | C
Inside surface temp. thermocouple, t2 = | 20 | C
Calculations
Heat convection, air layer, Q = | h * A * (t1 - t2) | Watts
h = | Q / (A*(t1 - t2))
S.I. Answer: h = | 5.5188 | W/m^2*C
h = | (W/m^2*K)/5.596
U.S. Answer: h = | 0.9862 | Btu/hr-ft^2*F
Boundary layer thickness = | X | mm
Air flow velocity = | V | m / s
Convective Heat Transfer Coefficient
Convective heat transfer coefficient, h = | k*C*(Gr*Pr)^n / L
Description | Length L |  | Gr | C | n
Vertical Plate |  |  | < 10^4 | 1.36 | 0.2
or |  |  | 10^4<10^9 | 0.59 | 0.25
Vertical Cylinder | 2*π*r |  | 10^9<10^12 | 0.13 | 0.333
Horizontal Plate | (S1 + S2) / 2 |  | 10^5<2*10^7 | 0.54 | 0.25
hot surface facing up |  |  | 2*10^7<3*10^10 | 0.14 | 0.333
Horizontal Plate |  |  | 3*10^5<3*10^10 | 0.27 | 0.25
hot surface facing down
Convective Heat Transfer Coefficient Calculation - Pick Horizontal or Vertical Plate:
Characteristic Length L | Input Data-1
height = | 8 | in
width = | 6 | in
Exterior surface temperature, Ts = | 146 | deg C
Ambient (room) temperature, Ta = | 36 | deg C
| Calculation |  |  |  | P1
Length, L=(height x width) / (height + width) = L = | 3.4286 | in
Plate characteristic length, L = | 0.087086 | m
Answer: Ts - Ta = | 110 | deg C
Th = | (Ts + Ta) / 2 | deg C
Answer: Th = | 91 | deg C
Air Properties at temperature, Th, from table below:
Input Data-2
Air conductivity, k = | 0.03115 | W / m*C
Air density, ρ = | 0.964 | kg / m^3
Air dynamic viscosity, μ = | 2.15e-05 | kg / sec*m
Boundary layer volume coefficient of expansion, β = | 0.00274 | 1 / deg C
Gravitational constant, g = | 9.81 | m/sec^2
Prandtl number, Pr = | 0.694 | -
Grashof number, Gr = | L^3*g*β*ρ^2*(Ts - Ta) / μ^2
Answer: Gr = | 3925817.967
Answer: Gr*Pr = | 2724517.6691
C and n below are found in the table above for the Gr*Pr value calculated here.
Input Data-3
Gr*Pr = | 10^3 < 10^9
C = | 0.53
n = | 0.25
Nusselt Equation, Air Film Coefficient, h = | k*C*(Gr*Pr)^n / L
S.I. Answer: h = | 7.7021 | W / m^2*C
U.S. Answer: h = | (W/m^2*K)/5.5956 | Btu/hr-ft^2*F
U.S. Answer: h = | 1.3765 | Btu/hr-ft^2*F
P2
CONDUCTIVITIES & DENSITIES
Properties at 68 deg F
MATERIAL | ρ | K | K
| lbm/ft^3 | Btu/hr-ft-F | W/m*C
Copper, pure | 559 | 223 | 386
Brass, 70 Cu, 30 Zn | 532 | 64 | 111
Silver, 99.9% pure | 657 | 235 | 407
Duralumin, 3-5%Cu, trace Mg | 174 | 95 | 164
Carbon Steel, 1.0%C | 487 | 25 | 43
Bronze, 75 Cu, 25 Sn | 541 | 15 | 26
Steel,18 Cr, 8 Ni | 488 | 9.4 | 16.3
Concrete, stone, 1-2-4 mix |  | 0.79 | 1.37
Glass, window |  | 0.45 | 0.78
Brick, common building |  | 0.4 | 0.69
Wood, fir |  | 0.063 | 0.109
Wood, white pine |  | 0.065 | 0.112
Glass Wool, 1.5 lb/ft^3 |  | 0.022 | 0.038
FINS
Fins are used to increase heat transfer area
and provide a cooling effect.
However, if h*A / P*k is greater than 1.00
the fins will insulate and prevent heat flow.
h = air film convective coefficient
A = exposed surface area of the fins.
P = perimeter of the fins.
k = fin material conductivity coefficient.
Case 1. Fin, finite length, heat loss by convection at end.
Heat flow rate, Q = | (K*Ab*n*ΔT)*X1 / X2
Input Data
Temperature at fin base, T1 = | 200 | deg F
Room Temperature, T2 = | 70 | deg F
Fin width, w = | 20 | in
Fin thickness, t = | 0.125 | in
Fin material thermal conductivity, K = | 174 | W/m*C
Convective heat transfer coefficient, h = | 5.7 | W / m^2*C
Fin length, L = | 0.75 | in
Number of fins, N = | 40
| Calculations |  |  |  | P3
Fin width, w = | 0.508 | m
Fin thickness, t = | 0.003175 | m
Fin base area, A = | w*t | m^2
A = | 0.0016129 | m^2
Temperature difference, ΔT = | T1 - T2
ΔT = | 130 | deg F
ΔT = | 54.4444 | deg C
For thin fin, n = | (2*h/K*t)^.5
n = | 4.5426
h / n*K = | 0.0072114
L = | 0.01905 | m
n*L = | 0.086537
sinh(n*L) = | 0.086645
cosh(n*L) = | 1.0037
X1 = | [(sinh(n*L) + (h / n*K)*cosh(n*L)]
X1 = | 0.00062717
X2 = | [(cosh(n*L) + (h / n*K)*sinh(n*L)]
X2 = | 1.0044
Q = | N*(K*A*n*ΔT)*(X1 / X2))
Answer: Q = | 1.7337 | Watts
Case 2. Fin, finite length (L) insulated end.
tanh(n*L) = | 0.086321
Heat flow rate, Q = | N*(K*A*n*ΔT)*tanh(n*L)
Answer: Q = | 239.6596 | Watts
Fin Efficiency
Ideal heat transfer occurs when the entire fin is at its base temperature.
Input Data
Temperature at fin base - Room Temperature, ΔT = | 20 | deg C
Fin material thermal conductivity, K = | 4 | W/ m*C
Convective heat transfer coefficient, h = | 9 | W / m^2*C
Fin width, w = | 30 | in
Fin thickness, t = | 0.08 | in
Fin length, L = | 0.75 | in
Calculations
Fin width, meters, w = | 0.762 | m
Fin thickness, meters, t = | 0.002032 | m
Fin base area, Ab = | w*t | m^2
Ab = | 0.0015484 | m^2
Fin length, meters, L = | 0.01905 | m
Two Fin face areas, Af = | 2*L*w
Af = | 0.029032 | m^2
Perimeter, P = | 2*(w + t)
P = | 1.5281 | m
n = | h*P/(K*Ab)
n = | 47.1219
n*L = | 0.89767 |  |  |  | P4
Fin efficiency, η = | Actual Q / Ideal Q
Q = (h*P*K*Ab)^.5*(ΔT)*(tanh(n*L)) = | (K*Ab*n)*(ΔT)*(tanh(n*L))
(h*P*K*A)^.5 = | (K*A*n)
Ideal heat transfer, Qa = | (h*P*K*A)^.5*ΔT*(tanh(n*L))
Qa = | 4.1744 | Watts
Ideal heat transfer, Qi = | (h*Af*ΔT)
Qi = | 5.2258 | Watts
η = | Qi / Qa
Answer: η = | 79.881 | %
Counter & Parallel Flow Heat Exchanger Tube Length Calculation
P5
Heat transfer, Q = | U*A*∆Tm
Plane wall heat transfer coefficient, U = | 1 / (1/ho + L/K + 1/h1
Cylindrical wall heat transfer coefficient, U = | 1 / (1/hi + [RoLn(Ro/Ri)]/K + Ri/Ro)
i and o refer to inside and outside tube surfaces.
Large temperature difference, ΔTbc = | Ta - Td
ΔTbc = | 20 | From Input Data below.
Small temperature difference, ΔTad = | Tb - Tc
ΔTad = | 52 | From Input Data below.
Logarithmic mean temp. difference, ΔTm = | (ΔTbc - ΔTad)/ln(Tbc/ΔTad)
Answer: ΔTm = | 33.4899 | deg C
The added resistance to heat transfer caused by corrosion is called fouling.
Fouling factor, R ranges between 0.0005 and 0.002. See manufactures data.
Fouling factor, R = | (1/Udirty) - (1/Uclean)
Forced Convection - in Coiled Tube Heat Exchangers
Turbulent flow in coiled tube. | Input Data
Temp. of water flowing in, Ta = | 78 | deg C
Temp. of water flowing out, Tb = | 74 | deg C
Tc = | 22 | deg C
Td = | 58 | deg C
Tube inside diameter, Di = | 51 | mm
Tube outside diameter, Do = | 54 | mm
Velocity of water in tube, V = | 3.5 | m / s
Water properties at temperature Tb deg C from the table above:
Water density, ρ = | 994.7 | kg / m^2
Cp = | 4.183 | k*J/kg*K
Water dynamic viscosity, μ = | 0.000682 | kg / m*s
Water conductivity, k = | 0.6283 | W / m*K
Prandtl number, Pr = | 4.51 | -
Factor, n = | 0.4
Velocity of water in tube, V = | 3 | m / s
Calculations
Water bulk temperature, Tb = | (Tin + Tout) / 2 | deg C
Answer: Tb = | 76 | deg C
Reynolds Number, Re = | V*D / ν
or, Re = | V*D*ρ / μ
Answer: Re = | 260343.0352 | Turbulent |  | Re >4000
Convective heat transfer coefficient, h = | 0.023*(Re^.8)*(Pr^n)*(k/d)
S.I. Answer: h = | 11128.3841 | W / m^2*K
U.S. Answer: h = | (W/m^2*K)/5.5956 | Btu/hr-ft^2*F
U.S. Answer: h = | 1988.6422 | Btu/hr-ft^2*F
S.I. Answer from above: h = | 11128.3841 | W / m^2*K
Large temperature difference, ΔTbc = | Tb - Tc
Answer: ΔTbc= | 52 | deg C |  |  | P6
Small temperature difference, ΔTad = | Ta - Td
Answer: ΔTad = | 20 | deg C
Logarithmic temperature difference, ΔTm = | (ΔTbc - ΔTad)/ln(Tbc/ΔTad)
Answer: ΔTm = | 33.4899 | deg C
Overall heat transfer coefficient = | Uo
Heat flow rate, Q = | Uo*A*ΔTm
Heat flow rate thru inside tube wall, Qi = | Uo*π*di*L*ΔTm
Heat flow rate thru outside tube wall, Qo = | Uo*π*do*L*ΔTm
Uo = | h *Ai / Ao
Tube inside area, Ai = | π*di*L
Tube outside area, Ao = | π*do*L
Overall heat transfer coefficient, Uo = | h *di / do
Answer: Uo = | 10510.1405 | W / m^2*K
Cp = | Cp*1000 | 1000*J/kJ
Answer: Cp = | 4183 | J/kg*K
Disregarding tube fouling, determine the tube length required:
The tube length required, L = | ρ*V*(di)^2*Cp*(Tout -Tin) / (4*Uo*do*ΔTm)
Answer: L = | 15.3733 | m
This is the end of this spread sheet.
P7

## RADIATION
HEAT TRANSFER SPREADSHEET CALCULATIONS |  |  |  | 4 PDH
Copy write, © Heat Transfer Spreadsheet Calculations by John R Andrew, 12 June 2011
RADIATION
Heat in the form of radiation travels through space at the speed of light.
Radiant heat energy is proportional to the 4th power of the absolute temperature.
Heat Radiation Upon a Surface
Fraction of heat energy absorbed, α = | absorbtivity
Fraction of heat energy reflected, ρ = | reflectivity
Fraction of heat energy passed thru., τ = | transmissivity | (transparent; solids, liquids, & gasses)
By definition, α + ρ + τ = | 1
Black Body Radiation
An ideal black body absorbs all incident
radiation so that, α = | 1
therefore, ρ = 0 and τ = 0
Input Data
t = | 22 | deg C
S.I. absolute temperature, Tk = | t + 273.2 | deg K
Answer: Tk = | 295.2 | deg K
Input Data
t = | 70 | deg F
U.S. absolute temperature, Tr = | t + 459.8 | deg R
Answer: Tr = | 529.8 | deg R
Radiation Example | Input Data
Material surface emissivity, e = | 0.91 | -
Stefan-Boltzmann constant, σ = | 5.6697e-08 | W / m^2-K^4
Dimension, L1 = | 20 | m
Dimension, L2 = | 3 | m
Surface temperature, t1 = | 38 | deg C
Calculation
Area, A = | L1*L2
Answer: A = | 60 | m^2
Absolute temperature. T = | C + 273
T = | 311 | deg Abs
Radiant thermal flux reflected, Q = | e*σ*T^4
Answer: Q = | 482.6619 | Watts |  |  | P1
Q is the radiant thermal flux per square foot reflected by the wall.
The total hemispherical heat radiation from
a black body surface (A) is, Eb = | σ*T^4 | W /m^2*K^4
Stefan-Boltzmann constant, σ = | 5.6697e-08 | W /m^2*K^4
Stefan-Boltzmann constant, σ = | 1.714e-09 | Btu/h*ft^2*R
Gray body radiation, Eg = | ε*σ*T^4 | W /m^2*K^4
Gray body radiation factor = | ε
Configuration or Emissivity Factor, CF = | E1 / E2
Radiation transmitted from surface 1 = | E1 | W /m^2*K^4
Radiation transmitted to surface 2 = | E2 | W /m^2*K^4
Surface 1 is smaller than surface 2.
If surface 2 completely surrounds
surface 1, Fa = | 1
Total radiation transmitted, Et = | ε*σ*CF*(T1^4-T1^4) |  | W /m^2*K^4
Radiation Example
Horizontal duct under a house.
What is the heat loss per unit area of the duct?
Input Data
Duct diameter, D = | 20 | cm
Duct surface temperature, tduct = | 85 | C
Duct emissivity, ε = | 0.8
Temperature under house, twalls = | 20 | C
Surrounding air temperature, tair = | 18 | C
Convective film coefficient, h = | 5.5 | W/ m^2*K | 0.96 | Btu/hr*ft^2*F
P2
1. Calculate heat lost by radiation: | Calculations
Stefan-Boltzmann constant, σ = | 5.6697e-08 | W /m^2*K^4
Tduct = | tduct + 273
Answer: Tduct = | 358 | deg K
Twalls = | twalls + 273
Answer: Twalls = | 293 | deg K
Surface 2 completely surrounds surface 1
Arrangement or Emissivity Factor, CF = | 1 | W/m^2*K^4
Heat transferred by radiation, Er = | ε*σ*CF*(T1^4 - T2^4)
Answer: Er = | 410.7566 | W/m^2*K^4
2. Determine heat lost by convection:
Convective heat transfer, Q / A = | h*(tduct - tair)
Answer: Q / A = | 368.5 | W / m^2
3. Add to find total heat loss:
Qtotal / Area = | Er + Q / A
Qtotal / Area = | 779.2566 | W / m^2
This is the end of this spread sheet.
P3

## MATH TOOLS
HEAT TRANSFER SPREADSHEET CALCULATIONS |  |  | 4 PDH
Copy write, © Heat Transfer Spreadsheet Calculations by John R Andrew, 12 June 2011
MATH TOOLS
Excel can be used to facilitate and document engineering calculations.
When using Excel's Goal Seek, unprotect the spread sheet by selecting:
Drop down menu: Tools > Protection > Unprotect Sheet > OK
When Excel's Goal Seek is not needed, restore protection with:
Drop down menu: Tools > Protection > Protect Sheet > OK
GOAL SEEK - Trial and Error by Excel Spread Sheet
T4 = 38.7 deg. C in the calculation below when input heat flow Q = 5.0 Watts.
The objective is to find the input heat Q that will result in the temperature T4 = 25 deg. C.
Excel spread sheets will make a trial and error iteration automatically with the tool called, "Goal Seek".
1. Select the calculated answer at red cell, T4 = 38.7 below.
2. Select: Tools > Goal Seek > Pick "To value:" > 25 > By changing: > Pick green cell, Q = 16.0 > Okay.
EXAMPLE - LOCKED
Input Data
Q = | 5 | Watts
A = | 0.25 | sq m
T1 = | 45 | deg. C
h1 = | 9 | W/sq m C
h2 = | 5 | W/sq m C
k = | 164 | W / m C
L = | 0.25 | m
Calculations
R1 = | 1 / h1 | sq m C/W
R1 = | 0.11111 | sq m C/W
R2 = | L / k | m*C / W
R2 = | 0.0015244 | m*C / W
R3 = | 1 / h2 | sq m C/W
R3 = | 0.2 | sq m C/W
Q / A = | (T1 -T4) / (R1 + R2 + R3)
T4 = | T1 - ((Q / A)*(R1 + R2 + R3))
Answer: T4 = | 38.7473 | deg. C
PROBLEM - UNLOCKED
Practice Goal Seek below: | Input Data
Q = | 15.9931 | Watts
A = | 0.25 | sq m
T1 = | 45 | deg. C
h1 = | 9 | W/sq m C
h2 = | 5 | W/sq m C
k = | 164 | W / m C
L = | 0.25 | m
Calculations
R1 = | 1 / h1 | sq m C/W
R1 = | 0.11111 | sq m C/W
R2 = | L / k | m*C / W
R2 = | 0.0015244 | m*C / W
R3 = | 1 / h2 | sq m C/W
R3 = | 0.2 | sq m C/W
Q / A = | (T1 -T4) / (R1 + R2 + R3)
T4 = | T1 - ((Q / A)*(R1 + R2 + R3))
Answer: T4 = | 25 | deg. C
EXCEL'S SOLVER > see 2D CONDUCTION
Step-1 Clik the "Excel Button" top left > Click "Excel Options".
This is the end of this spread sheet.
To install Solver, click the Microsoft Office Button, click Excel Options, and click Add-Ins. In the Manage box at the bottom of the window, select Excel Add-ins, and click Go. Check the Solver Add-in box in the Add-Ins dialog box, and click OK. After Solver is installed, you can run Solver by clicking Solver in the Analysis group on the Data tab.